## BE Nat. Risk scenarios
BE National Risk Scenarios
Scenario Group | ID # | Scenario Name | Description (initial condition, initiating events, evolution) | Risk (crisis scenario rating) | Impact | Likelihood | Description impact | Preventive measures | Curative measures
Cyberattack | 1A | Cyber attack on business critical ICT infrastructure of entities which are physically connected to the power grid like TSOs, DSOs, power plants and major (industrial) loads. | Attack against critical ICT systems of TSOs, DSOs, power plants and major industrial loads (e.g. central SCADA, substation SCADA, EMS, load-frequency control system, data storage, scheduling system, power plant's operating systems, office IT) The attacker(s) is/are able to enter one or more criticical ICT systems (TSO, DSO, Power Plant, Power Plant's operator or major loads). During this time the attacker(s) can act like an employee working the systems, meaning the attacker(s) can control & steer the system as well as deny access to regular users. | Major | Critical | Unlikely | Security of supply impacts: The attack will cause unintended outages of lines, transformers, power plants etc. with possible overloading on remaining lines and transformers and/or direct loss of supply. Could also cause unintendent outages of DSO lines and transformers within an amount of several thousand MWs (loss of supply) with effect on frequency or load flows in TSO's grid. Operational impacts: Will cause unintended outages of lines, transformers etc. with possible overloading on remaining lines and transformers. Structural or systemic degradation By manipulating set points of load frequency devices or sending wrong schedules towards market partners or power plants or switching off a huge amount of whole DSO's areas, the system frequency is changed with possible loss of load and/or power plants. Energy market impact: Market partners are possibly not able to follow schedules or to identify manipulated schedules.
| 1B | Cyber attack on business critical ICT infrastructure at market participants (not physically linked to the power grid) | Attack against the ICT systems of market participants not directly linked physically (e.g. market actors, power exchange platforms, market maker). The attacker(s) is/are able to enter one or more critical ICT systems of market participants. The attacker(s) can work the system as an employee during these moments, meaning the attacker(s) is/are controlling the ICT systems but also has/have the power to deny access to the system. | Major | Major | Possible | Operational impacts: The attacker is creating and sending manipulated schedules to other partners and/or can stop to send any schedules to others. The attacker can stop energy market functions so the market partner has to use bilateral back-up procedures. Power plants will follow wrong schedules and frequency /system balance is in danger. Corruption of control: Market operators or power exchange lose their control of the whole process and have to follow back-up procedures Security of supply: Possibly in danger if the TSOs are no longer able to balance the system with available reserve power. Structural or systemic degradation: The electricity system (balance) is in danger with the risk of a blackout. Energy market impact: The market is in danger to fulfil the task to offer access to buy and sell energy. Market partners are possibly not able to follow schedules or to identify manipulated schedules. In worst case, market may be suspended and replaced by other decision making mechanisms.
(physical) attack | 2A | Physical Attack against Critical Assets | Physical attack using vulnerabilities of power lines, transformers, substations, power plants, data centres. The attackers(s) destroy(s) techincal equipment in the TSO or DSO grid or power plants. It is possible this happens via several simultaneous attacks. | Major | Critical | Unlikely | Operational impacts: Grid operators have to react in order to restore n-1 security and to restore grid connections to partners. Unplanned usage of redispatch capabilities or reserve energy may be needed. Security of supply: The attack could directly cut load from the grid. The security of supply is in danger due to violations of n-1 security. Energy transport to regions with a lack of internal power plants is in danger and could lead to loss of load. Destroyed power plants are no longer able to fulfill load requests by market partners. TSOs are no longer able to activate reserve power plants and imbalance of load/production will lead to frequency deviations with automatic load shedding or power plant shedding. Infrastructure impacts: Destroyed assets are no longer available for energy transport and distribution. These assets have to be repaired, but the timeframe to do this is not clear. This maintenance possibly needs additional planned outages with a more risky situation for the security of supply. Structural or systemic degradation: Due to the amount of destroyed equipment, loss of load, loss of cross border lines, influence of frequency will happen. Loss of grid elements may cause overloads on other lines and also in other countries. Energy market impact: Market partners are possibly not able to follow schedules or have to reschedule energy trades due to missing connections to other countries or regions. Normal market activities could be stopped due to missing grid elements.
| 2B | Physical attack against Control Centres | Physical attack using vulnerabilities of control rooms or back-up control rooms of TSOs, major DSOs or major power plant operation centres. The attacker(s) attempt to destroy the main & back-up control centres of a TSO, major DSO or major power plant operation centre. | Major | Critical | Unlikely | Operational impacts: The grid or power plant operators are no longer able to monitor or steer the grid / power plants. Operational staff may have to be sent to substations or parts of the power plants to get information via telephone, thus receiving a very low level knowledge of current grid and power plant situation. Advice can be given by phone and have to be performed by staff in substations. Corruption of control: Full loss of control functions for the grids or power plants. Security of supply: Energy transport and delivery is still possible but in case of any actions needed to react to incidents, the Security of Supply will be in danger and possibly interrupted. Infrastructure impacts: destroyed control centres Structural or systemic degradation The "life" of the electricity grid is no longer under control. Due to missing advice and communication (online or by phone) to reserve power plants, loads or other TSOs, the ongoing "life" of the electricity grid could have overloads, frequency deviations etc.. Needed actions to secure the grid cannot be taken. Energy market impact: Market partners are possibly not able to follow schedules due to missing power plants. Market partners will not know immediately that the grid is no longer under control. The market cannot work with normal processes with the TSOs or power plants. TSOs / power plants are not able to interact with market partners. In worst case, market may be suspended and replaced by other decision making mechanisms.
Insider Attack | 3 | Insider Attack (through a cyberattack and/or physical attack) | Sabotage by employee/s or subcontractor/s via physical intervention or misuse of ICT systems. An employee(s) or subcontractor(s) takes control of the grid. In addition to controlling the grid, they can also physically destroy assets. | Major | Disastrous | Unlikely | Operational impacts: The whole operation of the grid is unstable because of the control take-over of the insider. This could lead to the shutting down of the entire grid. Security of supply: The insider might be able to shut down the entire grid. Infrastructure impacts: The insider is able to destroy infrastructure elements. Structural or systemic degradation: Multiple openings of transmission network elements Manipulation of markets managed by System Operator Energy market impact: Market partners are possibly not able to follow schedules or to identify manipulated schedules.
Extreme Weather | 4 | Storm | The forecasted storm increases in force over the last hour with expected average wind speeds > 150 km/h and wind gusts >200 km/h. Exceptionally strong wind gusts or local thunderstorms are causing vortexes and lightning strikes. The storm lasts several days and the repairs take time due to storm-damaged roads and the fact that many locations are difficult to reach. The large swaths of damage cause shortages of material, spare parts and personnel. | Major | Major | Likely | Transmission issues: Potential fragility of the grid integrity with an impact for end-users. Such impacts include: damages on lines due to wind and trees, damage to substations due to flying debris, automatic protection schemes triggering due to lighting to protect assets, pylons collapsing, many interconnectors operating close to security limits due to flows, internal and international transmission limitations, emergence of some internal islands and sensitive losses of transmission or distribution infrastructure potentially leading to load shedding or local/regional brownouts. Adequacy issue: There is a potential deficit in generation due to lower-than-expected wind output (due to high-speed shutdown and/or damage to windfarms or windfarm connections with possible unexpectedly long downtimes for those generators), unavailability of interconnectors and unavailability of distributed generation after damage to DSO grids.
| 5 | Winter Incident | Multiple overhead line faults as ice loading and/or sticky snow causes failed OHL insulators/fittings & dropped conductors. Tower failures due to snow & ice loading leads to multiple circuit tripping. | Major | Major | Possible | Operational and transmission security of supply issues: Faulted conductors and towers could cause fragmentation of the network and possible islanding. The duration of the repairs could extend beyond the immediate storm timescale: some roads and areas are impracticable and existing maintenance stock can be insufficient to replace all of the damaged equipment. The reaction time of line crews is increased because of blocked roads and dangerous environments. Security of supply impacts: Could lead to some loss of load or unacceptably low system voltages (brownout) as well as increased transmission congestions and a requirement for out-of-merit generation operation.
| 6 | Cold Spell | Cold temperatures around 10-20°C below seasonal average The water is freezing in reservoirs (lakes, rivers, other water reservoirs), and they are depleted. Lack of wind in forecast. An increase in demand due to cold weather, is observed. A decline in generation due to limited capacity to cool thermal PGMs (frozen cooling water resources) and/or operational problems with power generating modules’ equipment and frozen coal occurs in some countries. There are generation constraints due to reduced cooling capability of power generating modules and operational problems with power plant equipment. Hydro power plants decrease their output. Due to the climate conditions, some network elements are exposed to increased stress (icing, sagging, etc.) and reliability decrease. The situation lasts for a minimum of 3 weeks. | Major | Major | Possible | Operational impacts: There would be potential N-1 security issues, decreased security margin, an increased cascading disturbance probability and reduced transmission capacity. Load shedding may be required. The stress on power lines could lead to faults, and there could be difficulties to travel for personnel, inducing a higher response time and lower availability. The population could be asked to adapt its electricity consumption to reduce the peak load. There could be strong political pressure to maintain electric power for heating purposes. This pressure could also be in favour of stopping energy exports. Adequacy issue: It is expected that electricity prices could increase significantly. There would be a risk of load shedding to reduce the peak load.
| 7 | Heavy Precipitation & Flooding | Heavy rain for several days causes flooding of substations and power plants. There is a fast increase in water levels that were already very high. This causes flooding of power plants and substations. Landslides can also occur. Power plants are shut down and some substations are de-energized. Asset repairs cannot start until the water is gone and therefore can take up to a month. | Major | Major | Possible | Structural or systemic degradation: The scenario can result in flooding (and possibly landslides) of substations and power plants, and the weakening of tower foundations, as well as difficulties to travel for personnel, inducing a higher response time and their lower availability. Adequacy and security of supply impacts: There could be unexpected loss of load in the areas where the flooding is high enough to damage generation, transmission and/or distribution infrastructure.
| 8 | Dry Period & Heatwave | Combination of a heatwave 5 d > 30°C with expected peak temperatures > 38°C and an extremely dry period characterized by low rainfall. | Major | Major | Likely | Security of supply impacts: There may be load reduction and/or load shedding and generation reserves could be exhausted or very limited. The lack of generation capacity together with the lack of import capabilities leads to a scarcity situation, with the possiblity low hydro power production. There may be restrictions in the use of electricity for certain users during certain periods of time. Dry periods and low water levels can cause a lack of production. There may be alternating load shedding during some hours of the day due to the lack of production capacity. Operational impacts: The scenario may lead to non-fulfilment of N-1 criterion, applied redispatching and high voltage or voltage collapses on some parts of the network. Equipment faults due to heat can lead to equipment scarcity and long-term outages. Adequacy issues could lead to a voltage collapse. Structural or systemic degradation: There may be multiple planned outages for a few weeks and some unplanned outages due to equipment failure, as well as fast material deterioration.
Natural Disaster | 9 | Pandemic | International spread of disease. TSO Operating staff will be infected. The same situation at the power stations, power plants and DSOs which could lead to insufficient staff. | Minor | Minor | Possible | Operational impacts: Depending on the spread of the pandemic, the impacts on the power system may vary, but could include shutdowns of selected network elements, failures of power generation modules, loss of required reserves and balance problems in the power system leading to increased system operation costs. It could also lead to delimitations of asynchronous areas (transition to island mode), high system voltages due to low system demand during lockdown and an increased risk of human errors. Security of supply: There could be emergency load shedding or local power outages. Infrastructure impacts: There could be a possible decrease of the quality of the maintenance due to understaffing (rescheduling or prolongation of maintenance) as well as supply chain limitations for equipment and limited availability of contractor resources. There may also be a delay on new projects (new grid elements could be ready later) and an increased risk of human error (planning, operations, maintenance, etc.).
Technical failure | 10 | Simultaneous Failure of power system primary elements | The scenario is initiated by multiple grid elements failing at the same time (or very close together) independently of one another, resulting in N-1 security violation. Examples of this include faults on: • an HVDC cable causing the disconnection of a few power plants, • failures at substations or transmission lines, • N-1 violations not being detected due to inaccurate or incomplete modelling, • N-1 violations not being detected due to metering or monitoring failure, • a security standard violation due to operational error or control reaction not being fast enough. | Minor | Disastrous | Very unlikely | Security of supply impacts: There could be a shortage of electricity as well as frequency response being held on the system and therefore the resulting frequency deviation will trigger low frequency demand disconnection. Infrastructure impacts: Possible impacts on infrastructure include the loss of critical grid elements and possible cascading effects, leading to an unstable system. Operational impacts: There could be a limitation or total loss of availability of ancillary services as well as a risk of blackout. Operational impacts (most relevant for low load situations): Operational parameters (e.g. voltage, active power) go beyond operational security limits, and in extreme cases it can lead to a blackout.
| 11 | serial equipment failure due to a systematic defect | This scenario is initiated by some elements of the transmission or distribution network exhibiting abnormal behaviour that increase their risk of failure or lead directly to failure. An analysis finds that the root cause is a systematic failure in manufacturing, installation or maintenance. All elements of the same type or series are assumed to be susceptible to the same failure. All suspected elements are assumed unsafe but can't all be immediately replaced or repaired. | Minor | Major | Unlikely | Security of supply impacts: Multiple faults, especially occurring in a short period, may lead directly to power supply interruption, as well as cascading events and in extreme cases, to blackouts. If power plants (especially nuclear power plants) employ the same types of potentially faulty elements, there is a risk that they will need to be shut down as a preventive measure. If the faulty equipment is directly involved in supplying electricity to end-users, the supply may be affected immediately – either due to failures, or due to limitations imposed on operating conditions. Operational impacts: The electrical grid (and to some extent, other parts of the power system) may have to be operated on, despite the identified risk of failure for many months or even years - until most or all of the potentially faulty elements are replaced or repaired. Infrastructure impacts: There is high risk of damage to the power system infrastructure. A large investment may be required on the power system infrastructure to replace or repair faulty equipment. Emergency replacements or repairs may require other power system investments to be delayed or halted. Energy markets impact: Cross-border capacities made available for energy trade may have to be reduced, especially if the interconnections are affected directly by the faults. And energy trade may be limited if electricity demand is reduced due to forced or emergency demand curtailments.
| 12 | Loss of ICT tools or public telecommunication | The initiating event occurs either from the unavailability of a substantial part of telecommunication infrastructure used for power system or electricity market operation or from the unavailability of one or more ICT systems used in real-time planning and operation of the power system or energy market operation, due to technical failures. | Major | Critical | Unlikely | Security of supply impacts: There could be a possible use of forced (but controlled) disconnection as a remedial measure or a possible emergency disconnection of some demand or supply. In a worst-case scenario, a cascading event may be triggered. Energy markets impact: Market participants may initially suffer financial losses due to incorrect information or lack of access to some market data. Incorrect decisions of the market participants resulting from access to incorrect data may aggravate the situation in the power system. Disconnections will result in physical removal of some of the demand and/or supply from the market, and there could be a possible switch from market-controlled dispatch to a TSO-controlled dispatch. Consequential/related impacts: An emergency disconnection (especially a blackout) will result in potential other damages outside the electricity system.
| 13 | accidental (unintended) violation of N-1 criterion due to human error | The initiating event may be a mistake of the operator or service staff, leading to a cascading event due to human error. These N-1 violations or real-time constraints can occur on the grid as well as lead to cascading effects of other critical grid elements. | Minor | Major | Unlikely | The operational parameters (e.g. voltage, active power) could go beyond operational security limits. In extreme cases, it could lead to a system split.